# Industry Standard Practices for Protecting Island Mode Gas Turbine Generators from Overload and Flameout

Real and Reactive Power Availability: Island Mode vs. Grid-Parallel Operation

Prepared: April 2026

# Executive Summary

Island mode operation of gas turbine generators fundamentally differs from grid-parallel operation—not in thermal capability, but in control authority and protection strategy. When a gas turbine operates disconnected from the utility grid (island mode), it must independently maintain both frequency and voltage stability for the isolated power system. This imposes significant operational constraints that do not exist when connected to a strong grid.

Industry consensus across major OEMs (Kawasaki, GE, Siemens, Solar Turbines, Rolls-Royce) establishes a typical 10–15% power derate for island mode operation compared to grid-parallel capability at identical ambient temperatures. This derate is not thermal in nature—the turbine's combustion system and mechanical components can handle the same firing temperature and torque in either mode. Rather, it represents a control margin required to:

• Maintain transient response headroom (Incremental Reserve Margin)
• Prevent Dry Low Emissions (DLE) combustion flameout during load transients
• Preserve reactive power capability for voltage stability
• Enable safe load rejection without overspeed trip
• Support effective underfrequency load shedding (UFLS)

For the 15–30 MW class heavy-frame, simple-cycle turbines examined in this report, the island mode derate typically manifests as an operational ceiling of 85–90% of the ISO base rating, with additional considerations for step-load limitations, reactive power management, and combustion stability.

# Contents

1	Executive Summary	2

2	Contents	3

3	Introduction: Island vs. Grid-Parallel Operations	6

4	Fundamental Differences: Control and Stability Requirements	6

4.1	Grid-Parallel Operation	6

4.2	Island Mode Operation	7

5	Island Mode Derating: Magnitude and Rationale	8

5.1	The Nature of Island Mode Derate	8

5.1.1	Temperature Derate (Ambient Correction)	8

5.1.2	Island Mode Derate (Stability and Control)	8

5.2	Incremental Reserve Margin (IRM)	8

6	OEM-Specific Practices and Specifications	9

6.1	Kawasaki Heavy Industries (KHI)	9

6.1.1	L20A (GPB180D) - 18 MW Class	9

6.1.2	Combustion Mode Management	9

6.1.3	Control Philosophy	9

6.2	General Electric (GE) - Frame 5, Frame 6, LM Series	10

6.2.1	Frame 6B - 45 MW Class	10

6.2.2	Frame 5 - 25-30 MW Class	10

6.2.3	GE Island Mode Protection Features	10

6.2.4	Industry Experience	10

6.2.5	Load Acceptance Testing	10

6.3	Siemens Energy - SGT-400, SGT-800 Series	10

6.3.1	SGT-800 - 47.5 MW Class	11

6.3.2	Siemens Island Mode Design Philosophy	11

6.3.3	Reactive Power Management	11

6.3.4	Control Integration	11

6.4	Solar Turbines - Taurus, Mars, Titan Series	11

6.4.1	Taurus 60 - 5.3 MW (Mechanical Drive) / 6.0 MW (Power Generation)	11

6.4.2	Mars 100 - 10–11 MW Class	11

6.4.3	Titan 130 - 13.5 MW Class	11

6.4.4	Solar Island Mode Best Practices	12

6.5	Rolls-Royce / Siemens (Former Industrial RB211)	12

6.5.1	RB211 Series - 25–30 MW Class (Industrial/Aeroderivative Hybrid)	12

6.5.2	Island Mode Characteristics	12

6.5.3	Protection Philosophy	12

7	5. Protection and Control Strategies for Island Mode Operation	13

7.1	Governor Control Modes	13

7.1.1	Droop Control (Grid-Parallel)	13

7.1.2	Isochronous Control (Island Mode)	13

7.1.3	Isochronous Load Sharing	13

7.1.4	Control Mode Transition	13

7.2	Underfrequency Load Shedding (UFLS)	13

7.2.1	Typical UFLS Scheme (60 Hz System)	13

7.2.2	Design Considerations	14

7.2.3	Industry Example	14

7.3	Over-Excitation and Under-Excitation Limiting	14

7.3.1	Over-Excitation Limiter (OEL)	14

7.3.2	Mitigation Strategies	14

7.3.3	Under-Excitation Limiter (UEL)	15

7.3.4	Coordination with Island Mode Operation	15

7.4	Rate-of-Change-of-Frequency (ROCOF) Protection	15

7.4.1	ROCOF Applications in Island Mode	15

7.4.2	Typical Settings	16

8	Combustion System Considerations: DLE and Flameout Prevention	16

8.1	Dry Low Emissions (DLE) Technology	16

8.1.1	Challenges in Island Mode	16

8.1.2	Step Load Limitations	16

8.2	Combustion Mode Management	17

8.2.1	DLE/Premix Mode	17

8.2.2	Diffusion Mode	17

8.2.3	Automatic Mode Switching	17

8.2.4	Island Mode Implications	17

9	Reactive Power and Voltage Control	17

9.1	Power Factor Correction	18

9.2	Voltage Droop Control	18

9.3	Synchronous Condensers	18

9.4	Static VAR Compensators (SVC	18

9.5	Typical Island Mode Power Factor	18

10	Comparative Analysis: OEM Island Mode Practices	19

11	Strategies to Maximize Usable Island Mode Power	19

11.1	Power Factor Correction	20

11.2	Advanced Load Shedding Schemes	20

11.3	Coordinated Multi-Unit Operation	20

11.4	Energy Storage Integration	20

11.5	Load Management and Demand Response	20

11.6	Governor and Excitation System Tuning	20

11.7	Combustion Control Optimization	20

11.8	Key Principle	20

12	Conclusions and Industry Best Practices	21

12.1	Summary of Key Findings	21

12.1.1	Universal Industry Practice	21

12.1.2	Physical Basis	21

12.1.3	Typical Operating Limits	21

12.1.4	Combustion Stability Critical	21

12.1.5	Incremental Reserve Margin	21

12.2	Best Practices for Island Mode Operation	21

12.2.1	Design Phase	21

12.2.2	Operational Phase	22

12.2.3	Control System Requirements	22

12.2.4	Maintenance and Testing	22

13	References	23

# Introduction: Island vs. Grid-Parallel Operations

Gas turbine generators serve as critical power sources in both grid-connected and isolated (island mode) applications. While the physical hardware remains identical, the operational dynamics differ markedly between these two modes. Understanding these differences is essential for power system designers, operators, and planners, particularly in applications such as:

- Remote industrial facilities (oil & gas production, mining)

- Microgrids and distributed generation systems

- Emergency backup and black-start capability

- Critical infrastructure requiring high reliability

In grid-parallel operation, a large utility grid acts as an "infinite bus," absorbing power swings and providing strong voltage and frequency support. The grid's massive inertia and distributed generation capacity buffer sudden load changes, allow generators to operate near their rated capacity (adjusted only for ambient conditions), and supply unlimited reactive power for voltage regulation.

In island mode operation, a gas turbine generator operates independently of the wider grid, directly supplying a localized power network. The turbine becomes solely responsible for maintaining both frequency (speed) and voltage control for the islanded system. There is no external grid to share load transients or reactive power demand, significantly increasing the risk of destabilizing events such as:

- Frequency excursions leading to underfrequency load shedding or overspeed trips

- Voltage collapse from inadequate reactive power support

- Combustion instability and flameout, especially in Dry Low Emissions (DLE) systems

- Generator thermal limits being exceeded due to high reactive loading

The central question addressed in this report is: How much power can safely be extracted from a gas turbine generator in island mode, and what industry-standard practices enable operators to maximize this capability while maintaining reliability?

# Fundamental Differences: Control and Stability Requirements

## Grid-Parallel Operation

When connected to a strong utility grid, the gas turbine generator operates with:

- Reactive Power Support: The grid provides essentially unlimited reactive power (VAR) support. The generator's automatic voltage regulator (AVR) maintains terminal voltage, but if the generator approaches its reactive capability limit, the grid seamlessly supplies additional VARs. The generator can operate at or near unity power factor with minimal concern for voltage stability.

- Load Transients: Sudden load applications (motor starts, load steps) are immediately shared across all online generation. The grid's low impedance and high short-circuit capacity ensure that the increment seen by any individual generator is small and gradual. Governor response times of 5–10 seconds are generally adequate.

- Thermal Margin: Generators can operate continuously at or near their thermal limits (firing temperature, turbine inlet temperature) because the grid buffers transients and provides time for thermal control systems to respond.

## Island Mode Operation

Island mode operation imposes dramatically different requirements:

- Frequency Control: The islanded turbine(s) must independently maintain system frequency. Any load-generation mismatch immediately manifests as a frequency deviation, governed by the swing equation:

dfdt=dωdt=Pmech-Pelec2×H

Where:

df/dt represents the rate of change of frequency

dω/dt represents the rate of change of angular speed

Pmech ​ is the mechanical input power

Pelec ​ is the electrical air-gap output power

H is the inertia constant of the rotating machine (typically 3–6 seconds for gas turbines)

All power quantities are expressed on a common per-unit base, such that the resulting rate of change of frequency is obtained in per-unit per second.

Small inertia means rapid frequency changes—a 10% load step can cause frequency excursions of 1–2 Hz within the first second if not properly managed.

- Reactive Power Responsibility: All reactive power must be supplied by the islanded generator(s). The generator capability curve becomes a hard constraint—operating too far into the lagging (overexcited) or leading (underexcited) regions can cause:

  - Rotor overheating (over-excitation limiter trip)

  - Loss of synchronism (under-excitation limiter trip)

  - Voltage instability

- Load Transient Sensitivity: Every load change is a system event. A large motor start or sudden load application represents a step change that the turbine must absorb entirely. Insufficient incremental reserve margin (IRM) leads to:

  - Rapid frequency decay

  - Governor saturation (fuel valve fully open)

  - Potential flameout if combustor pressure ratio falls too rapidly

- Thermal and Combustion Constraints: DLE combustion systems operate within a narrow equivalence ratio band. Rapid load transients can force the combustor lean (risking lean blowout/flameout) or rich (increasing emissions, potentially requiring mode switch to diffusion combustion). The turbine must maintain sufficient margin to handle transients without compromising combustion stability.

# Island Mode Derating: Magnitude and Rationale

## The Nature of Island Mode Derate

It is critical to understand that island mode derating is fundamentally different from temperature derating.

### Temperature Derate (Ambient Correction)

As ambient temperature rises above ISO conditions (15°C, 1.013 bar, 60% RH), air density decreases, reducing mass flow through the compressor. This directly reduces the turbine's thermal output capability—less air means less fuel can be burned at the design firing temperature. This derate applies equally to both grid-parallel and island modes. A turbine rated at 20 MW at ISO conditions might produce only 16–17 MW at 40°C ambient, regardless of operating mode.

### Island Mode Derate (Stability and Control)

The island mode derate is imposed on top of any temperature effects. At a given ambient temperature, the turbine's usable power in island mode is limited below the thermal maximum. This limitation is not about exceeding firing temperature or mechanical stress—it's about maintaining stable, controllable operation. Industry practices dictate holding 10–15% headroom below the thermal capability to accommodate:

- Load fluctuations without unacceptable frequency excursions or protective trips

- Reactive power demands that consume generator apparent power capacity

- Step load changes within combustion stability limits to prevent flameout

- Load rejection capability without exceeding overspeed limits

- Incremental reserve margin for frequency regulation

The magnitude of this derate varies by application, OEM, and system design, but converges around 10–15% for most industrial applications.

## Incremental Reserve Margin (IRM)

A key concept in island mode operation is the Incremental Reserve Margin (IRM)—the amount of additional power a turbine can deliver in a short timeframe (typically 5–10 seconds) in response to a sudden load increase. IRM is distinct from spinning reserve:

| Spinning Reserve | The difference between present output and maximum continuous capability, available given sufficient time (minutes). |
| --- | --- |
| Incremental Reserve Margin | The increase in output achievable within seconds, limited by governor response, fuel system dynamics, and combustion system constraints. |

Industry guidelines suggest gas turbines should typically be capable of providing:

- Immediate response: 10–15% of rated capacity within 1–2 seconds

- Short-term capacity: Additional 0.5–1.0% of rated capacity per second thereafter

- Total response: Approaching thermal limits within 10–30 seconds, depending on starting load

For a 20 MW turbine operating at 18 MW (90%) in island mode with a 2 MW load step:

- Immediate IRM (15%): 3 MW available → adequate to cover the step

- Frequency will dip initially as mechanical power lags electrical demand

- Governor opens fuel valve, increasing firing temperature and power

- Frequency recovers as mechanical power catches up, typically within 5–10 seconds

Operating at higher base loads reduces IRM. At 95% load, only 1 MW of immediate reserve exists—a 2 MW step would cause severe frequency decay, likely triggering underfrequency load shedding or protective trips.

# OEM-Specific Practices and Specifications

## Kawasaki Heavy Industries (KHI)

Kawasaki's approach to island mode operation for their L20A and M7A series turbines (18–30 MW class) demonstrates industry-standard protective practices:

### L20A (GPB180D) - 18 MW Class

- ISO Base Rating: ~18 MW (at 15°C, sea level)

- Recommended Island Mode Maximum: ≤90% of full load (~16.2 MW at ISO conditions)

- Island Mode Derate: 10% explicit margin for stability and transient response

- Maximum step load increase: +25% of full load

- Maximum step load decrease: –15% of full load (controlled)

- 100% step unloading acceptable for emergency trip scenarios

- Load must be held for N minutes after N MW step loading (e.g., 1.5 min hold after 1.5 MW step)

### Combustion Mode Management

- DLE (Dry Low Emissions) operation: Preferred mode for NOx <15 ppm

- Automatic shift to diffusion combustion during large transients to prevent flameout

- Recommended to maintain ≥50% load to stay in DLE mode during island operation

### Control Philosophy

- Isochronous governor control in island mode for frequency regulation

- Automatic transition between droop (grid-parallel) and isochronous (island) modes

- Requires grid status signals for mode detection (switchgear position, frequency deviation)

- KHI documentation explicitly states: "Generator load must be immediately shed to below turbine full load, otherwise the turbine may shutdown due to overload" when transitioning to island mode, reinforcing the need for continuous load management and headroom.

## General Electric (GE) - Frame 5, Frame 6, LM Series

GE's extensive portfolio of gas turbines includes several models well-suited for island mode operation, particularly the Frame 5 (25–30 MW), Frame 6B (45 MW), and LM2500 aeroderivative (25–30 MW) series.

### Frame 6B - 45 MW Class

- Island Mode Capability: Explicitly designed and marketed for island mode operation

- Typical Operating Limit: 85–90% of base rating in island applications

- Black-start capable with appropriate auxiliary systems

### Frame 5 - 25-30 MW Class

- Proven reliability in remote, island mode installations

- Step load capability: Industry-standard ~25% step acceptance

- Governor response optimized for islanded operation with fast fuel scheduling

### GE Island Mode Protection Features

- Advanced combustion control with rapid fuel staging

- Over-excitation and under-excitation limiters coordinated with capability curves

- Load rejection capability with overspeed protection systems

- UFLS (underfrequency load shedding) coordination with governor response

### Industry Experience

GE turbines have demonstrated successful island mode operation in numerous oil & gas applications worldwide. The Frame 6B is particularly noted for its robust performance in isolated systems, with documented cases of continuous operation in island mode at remote production facilities. GE's control philosophy emphasizes maintaining 10–15% power margin below thermal limits specifically for transient response capability.

### Load Acceptance Testing

GE typically specifies block load acceptance tests during commissioning for island-mode projects, demonstrating the ability to accept step loads up to 25% of rated capacity while maintaining frequency within ±3% and recovering to steady-state within 10–15 seconds.

## Siemens Energy - SGT-400, SGT-800 Series

Siemens Energy's industrial gas turbine portfolio includes the SGT-400 (10–15 MW) and SGT-800 (47–50 MW) twin-shaft engines, both designed for island mode applications.

- SGT-400 Twin-Shaft - 12.9 MW (Power Generation)

- ISO Simple Cycle Output: 12.9 MW (electric)

- Mechanical Drive Configuration: Up to 14.9 MW (shaft power)

- Island Mode Operational Practice: 85–90% of rated output for continuous operation

- Twin-shaft design provides inherent load-following flexibility

### SGT-800 - 47.5 MW Class

- ISO Simple Cycle: 47.5 MW (50 Hz) / 50.5 MW (60 Hz)

- Proven reliability: 99.1% availability across 620+ installations

- DLE combustion with fuel flexibility (up to 30 vol% hydrogen capability)

### Siemens Island Mode Design Philosophy

- Emphasis on fuel flexibility and combustion stability across load range

- Advanced DLE systems with automatic mode switching to maintain emissions compliance

- 10–15% typical derate from grid-parallel to island continuous rating

- Step loading managed through control system with combustion mode coordination

### Reactive Power Management

Siemens specifies generator capability curves with clear overexcitation and underexcitation limits. In island mode, reactive droop compensation is recommended for multi-unit installations, with voltage droop typically set at 2–4% for stable VAR sharing. For single-unit island operation, automatic voltage control maintains setpoint within ±0.5%.

### Control Integration

Siemens SPPA-T3000 control system (or equivalent) provides:

- Integrated governor and excitation control

- Automatic island detection and mode switching

- Coordinated load shedding interfaces

- Combustion mode management (DLE/diffusion transition logic)

## Solar Turbines - Taurus, Mars, Titan Series

Solar Turbines (a Caterpillar company) specializes in industrial turbines for oil & gas and power generation, with extensive island mode experience.

### Taurus 60 - 5.3 MW (Mechanical Drive) / 6.0 MW (Power Generation)

- Twin-shaft design with excellent part-load efficiency

- Island mode operation standard in many oil & gas applications

- Typical island derate: 10–15% below continuous rating for transient margin

### Mars 100 - 10–11 MW Class

- Industrial workhorse with proven reliability in remote installations

- DLE combustion with SoLoNOx technology

- Step load acceptance: Up to 25% with appropriate governor tuning

### Titan 130 - 13.5 MW Class

- Heavy-duty industrial design

- Island mode capability with fast load response

- Integrated control packages available for island applications

### Solar Island Mode Best Practices

Solar emphasizes system-level design for island applications:

- Load shedding schemes coordinated with governor response time

- Reactive power margins maintained at 15–20% of generator MVA rating

- UFLS set points typically at 58.5 Hz (first stage), 57.5 Hz (second stage) for 60 Hz systems

- Governor tuning for isochronous operation with deadband minimized (<0.1 Hz)

Solar's published literature consistently recommends operating island mode systems at 80–90% of continuous rating to preserve transient response capability, with higher loading permitted only when load is known to be stable (non-variable industrial processes).

## Rolls-Royce / Siemens (Former Industrial RB211)

Rolls-Royce's industrial gas turbine business was acquired by Siemens in 2014, but legacy Rolls-Royce turbines remain in widespread use.

### RB211 Series - 25–30 MW Class (Industrial/Aeroderivative Hybrid)

- High efficiency and rapid load response

- Island mode capability well-established in offshore oil & gas platforms

- Typical island operation: 85–90% of base rating

### Island Mode Characteristics

- Aeroderivative heritage provides fast transient response (better than heavy-frame units)

- DLE combustion with automatic mode management

- Step load capability: 30–35% (higher than heavy-frame turbines due to faster response)

### Protection Philosophy

- Emphasis on thermal monitoring and exhaust temperature spread

- Coordinated excitation limiting to prevent generator overheating during reactive loading

- Load rejection testing typically demonstrates successful 100% load dump without trip

The RB211's faster response and higher power-to-weight ratio compared to heavy-frame turbines allows slightly higher island mode loading (90–95%), but industry practice still maintains 10% margin for unforeseen transients.

# 5. Protection and Control Strategies for Island Mode Operation

## Governor Control Modes

### Droop Control (Grid-Parallel)

When connected to the grid, turbines operate in droop mode, where speed (frequency) decreases linearly with increasing load according to a preset droop characteristic (typically 3–5%). Multiple turbines on droop automatically share load proportionally. The grid dictates frequency, and each turbine finds its equilibrium load point based on its droop setting and the system frequency.

### Isochronous Control (Island Mode)

In island mode, at least one turbine must operate in isochronous (zero-droop) mode to maintain system frequency at the setpoint (typically 60.0 Hz). The governor actively adjusts fuel flow to keep speed constant regardless of load changes (up to the turbine's capability limits). This provides tight frequency regulation but requires the turbine to have adequate headroom to respond to load increases.

### Isochronous Load Sharing

When multiple turbines operate in island mode together, isochronous load sharing via communication links (load-sharing lines or peer-to-peer digital communication) allows all units to maintain constant frequency while proportionally sharing load. Each turbine's governor communicates its load and adjusts fuel flow to balance the system. This is more complex than droop but provides better frequency regulation and allows flexible load distribution.

### Control Mode Transition

Modern control systems automatically detect grid loss and transition from droop to isochronous mode. This transition must be carefully managed to avoid:

- Frequency overshoot or undershoot during mode switch

- Governor saturation if base load is too high for available headroom

- Hunting or oscillation if multiple units switch modes simultaneously without coordination

## Underfrequency Load Shedding (UFLS)

UFLS is the primary protection mechanism for preventing total system collapse during island mode operation when generation is insufficient to meet load.

### Typical UFLS Scheme (60 Hz System)

| Stage 1 | 59.0 Hz | Shed 15% of non-critical load, 0.5 second time delay |
| --- | --- | --- |
| Stage 2 | 58.5 Hz | Shed additional 15% of load, 0.5 second delay |
| Stage 3 | 58.0 Hz | Shed additional 15% of load, 0.3 second delay |
| Stage 4 | 57.5 Hz | Shed remaining non-critical load, 0.1 second delay |

### Design Considerations

Load Prioritization: Critical loads (control systems, safety systems, essential processes) are never shed. Non-critical loads are prioritized and assigned to UFLS stages based on operational importance.

Rate-of-Change-of-Frequency (ROCOF) Adaptive Shedding: Advanced schemes measure df/dt in addition to absolute frequency. If frequency is falling rapidly (e.g., >0.5 Hz/sec), indicating a large generation loss, UFLS can trigger at higher frequency thresholds to arrest the decline before reaching critical levels.

Coordination with Governor Response: UFLS setpoints must be coordinated with expected governor response times. Typical gas turbine governors require 5–10 seconds to fully respond to a frequency deviation. UFLS must allow sufficient time for governor action before shedding load, but not so much time that frequency falls below equipment safe operating limits (typically 57 Hz minimum for 60 Hz systems).

Load Restoration: After UFLS activation, loads should not automatically reconnect. Operators must manually assess system stability and gradually restore loads to avoid re-triggering UFLS or overloading the turbine.

### Industry Example

In the Indonesian case study reported by Hamilton et al. (2009), a 105 MW turbine trip in an island system triggered multi-stage UFLS, but inadequate shedding magnitude and delayed response resulted in system collapse despite having apparent spinning reserve. This highlighted the importance of properly sizing UFLS stages relative to expected generation losses and coordinating with actual governor response dynamics.

## Over-Excitation and Under-Excitation Limiting

Generator reactive capability is constrained by thermal limits (rotor heating, stator heating) and stability limits (pull-out torque). Excitation limiters protect the generator from operating outside safe regions of the capability curve.

### Over-Excitation Limiter (OEL)

Protects against excessive field current (rotor overheating) when the generator supplies large amounts of lagging reactive power (inductive loads, low power factor). In island mode, heavy motor loads can drive the generator into over-excitation. The OEL monitors field current and field voltage; if limits are exceeded for a preset time (typically 10–30 seconds for thermal protection), the OEL reduces excitation, which lowers terminal voltage. This can cause voltage collapse if the system has insufficient reactive power support.

### Mitigation Strategies

Operate at higher power factor (minimize reactive load)
- Install capacitor banks or synchronous condensers for reactive support
- Size generators with adequate MVA rating for expected reactive demands
- Monitor power factor and reactive loading in real-time

### Under-Excitation Limiter (UEL)

Prevents loss of synchronism when the generator operates at leading power factor (capacitive, supplying negative VARs). This can occur during light load conditions with long cables or lightly loaded transformers. The UEL increases excitation if the generator approaches the stability limit, maintaining synchronism.

### Coordination with Island Mode Operation

In island mode, the generator must supply all system reactive power. Operating near either limit (OEL or UEL) constrains real power capability because:

S2=P2+Q2

Where:

S denotes the apparent power in megavolt-amperes (MVA)

P denotes the real (active) power in megawatts (MW)

Q denotes the reactive power in megavolt-amperes reactive (MVAr)

If a 20 MVA generator is supplying 8 MVAR of reactive power, we can find maximum real power by rearranging the equation as P2 = S2 – Q2 and substituting:

Pmax=202-82=400-64=336≈18.3

Even though the turbine may be thermally capable of 20 MW, generator reactive loading limits real output to 18.3 MW in this example. This is another reason for the island mode derate—preserving reactive capability reduces real power constraints.

## Rate-of-Change-of-Frequency (ROCOF) Protection

ROCOF relays (df/dt relays) detect rapid frequency changes that indicate significant generation-load imbalances. While primarily used for anti-islanding protection in distributed generation, ROCOF principles apply to load shedding in controlled island systems.

### ROCOF Applications in Island Mode

Adaptive Load Shedding: If df/dt exceeds a threshold (e.g., 0.5 Hz/s), indicating a large generation loss, accelerated UFLS can be triggered at higher frequency levels than standard UFLS.

Generator Trip Detection: Monitoring df/dt allows the control system to distinguish between slow load increases (gradual frequency decay) and sudden generation trips (rapid frequency decay), enabling appropriate response.

Islanding Detection: When transitioning from grid-parallel to island mode, ROCOF can detect the separation event and trigger automatic mode changes and load adjustments.

### Typical Settings

- ROCOF threshold: 0.3–1.0 Hz/s (depending on system inertia)

- Time window: 100–500 milliseconds for rate calculation

- Coordination with standard underfrequency relays to avoid nuisance tripping

# Combustion System Considerations: DLE and Flameout Prevention

## Dry Low Emissions (DLE) Technology

Modern gas turbines employ DLE combustion to meet stringent NOx emission regulations (typically <15–25 ppm) without water or steam injection. DLE systems operate with lean, premixed combustion—excess air dilutes the flame, reducing peak combustion temperatures and thus NOx formation.

DLE Operating Principles

- Fuel and air are premixed upstream of the combustion zone

- Combustion occurs at lower equivalence ratios (ϕ < 0.6–0.7)

- Multiple fuel stages allow load-range optimization

- Flame stabilization requires careful control of fuel-air mixture

### Challenges in Island Mode

DLE combustion operates within a narrow stability envelope. Rapid load transients can upset the fuel-air ratio, risking lean blowout (LBO) or flameout. Key concerns include:

- Load Rejection: Sudden loss of electrical load causes rapid turbine acceleration. Fuel flow must decrease rapidly to prevent overspeed, but reducing fuel too quickly can drop the combustor below the lean stability limit, causing flameout.

- Large Load Steps: Step load increases require rapid fuel addition. If fuel flow increases too fast relative to airflow (which lags due to compressor inertia), the combustor can become momentarily rich, causing combustion dynamics, pressure oscillations, or requiring mode shift to diffusion combustion.

- Low-Load Operation: At low loads (<50% for many DLE systems), maintaining stable premixed combustion becomes difficult. Many turbines automatically shift to diffusion (non-premixed) combustion below a threshold load, sacrificing emissions for stability.

### Step Load Limitations

Industry practice limits step loads to 25% of rated capacity specifically to maintain DLE combustion stability. Exceeding this limit typically triggers automatic mode switching:

- +25% step load: System remains in DLE with active control compensation

- +30–40% step load: Automatic shift to diffusion mode to prevent flameout

- Load shedding >25%: May shift to diffusion mode temporarily during transient

Protection Strategies

- Fuel staging schedules optimized for transient response

- Active combustion dynamics monitoring (pressure sensors, acoustic detection)

- Automatic diffusion mode backup when DLE stability is threatened

- Load rate limiters in control system (typically 1–2 MW/minute for ramping)

## Combustion Mode Management

Most modern DLE turbines can operate in multiple combustion modes:

### DLE/Premix Mode

- Primary mode for emissions compliance

- NOx: 15–25 ppm (at 15% O₂)

- Load range: Typically 50–100% load

- Requires stable fuel supply and controlled load transients

### Diffusion Mode

- Backup mode for stability or low-load operation

- NOx: 50–150 ppm (higher emissions)

- Load range: Start-up through full load

- More tolerant of transients and fuel quality variations

### Automatic Mode Switching

Modern control systems automatically select combustion mode based on:

- Turbine load level

- Rate of load change

- Combustion dynamics monitoring (pressure oscillations)

- Fuel quality parameters

- Ambient conditions

### Island Mode Implications

In island operation, the control system must balance emissions compliance (DLE preferred) with reliability (diffusion more stable). Recommended practices:

- Maintain loads >50–60% to stay in DLE mode when possible

- Allow automatic diffusion mode during large transients

- Plan load shedding to keep remaining load in DLE-compatible range

- Accept higher emissions during transient events to preserve system stability

# Reactive Power and Voltage Control

Island Mode Reactive Power Management Strategies:

## Power Factor Correction

- Install capacitor banks (switched or fixed) to supply leading VARs

- Size capacitors for typical load power factor (e.g., 0.85 lag)

- Reduce generator reactive burden, freeing capacity for real power

## Voltage Droop Control

- Set AVR with reactive droop (typically 2–5%)

- As reactive load increases, voltage decreases slightly

- Provides self-regulating characteristic: lower voltage reduces reactive demand

- Essential for multi-unit island operation to share VARs

## Synchronous Condensers

- Dedicated synchronous machines for reactive support

- Can provide both lagging and leading VARs

- Add system inertia, improving frequency stability

- Expensive but effective for large island systems

## Static VAR Compensators (SVC

- Fast-acting thyristor-controlled reactive compensation

- Can regulate voltage more precisely than capacitors

- Higher cost but beneficial for dynamic loads (large motors)

## Typical Island Mode Power Factor

Industry practice targets 0.90–0.95 power factor (lagging) for island mode operation. This provides:

- Adequate reactive margin for motor starts and transients

- Generator capacity mostly allocated to real power

- Acceptable voltage regulation

Example: 20 MW of real power at 0.92 PF:

Reactive Power =Q=P×tancos-1pf

Q=20×tancos-10.92

= 20 ×0.426

=8.5 MVAr

Apparent Power =S=200.92=21.7 MVA

This requires a generator rated for at least 22 MVA to accommodate both real and reactive loading with margin.

# Comparative Analysis: OEM Island Mode Practices

Table 1: OEM Comparison of Island Mode Derating and Protection Practices

| OEM / Model | Power Class (MW) | Island Mode Derate (%) | Max Step Load (%) | DLE Capability | Control Features | Reactive Support |
| --- | --- | --- | --- | --- | --- | --- |
| Kawasaki L20A | 18–20 | 10% (90% max continuous) | ±25% / -100% | DLE standard, auto diffusion backup | Isochronous/droop, auto mode switch | Voltage droop 2–4%, OEL/UEL |
| Kawasaki M7A-03 | 7–8 | 10–15% (85–90% max) | ±25% | DLE with mode management | Twin-shaft design, fast response | Standard AVR control |
| GE Frame 6B | 45 | 10–15% (85–90% typical) | ~25% | DLN combustion | Island-optimized controls, black-start capable | Advanced excitation system |
| GE Frame 5 | 25–30 | 10–15% | ~25% | DLN available | Proven island reliability | Standard coordination |
| GE LM2500+ | 25–30 | 10% | 30% (aeroderivative) | DLE capable | Fast transient response | High power density |
| Siemens SGT-400 | 12.9 (elec) | 10–15% | 25% | DLE with fuel flexibility | Twin-shaft, SPPA-T3000 controls | Reactive droop 2–4% |
| Siemens SGT-800 | 47.5–50.5 | 10–15% | 25% | Enhanced DLE, H₂ ready | 99.1% reliability, advanced controls | Full capability curve mgmt |
| Solar Taurus 60 | 5.3–6.0 | 10–15% | 25% | SoLoNOx DLE | Twin-shaft flexibility | Integrated packages |
| Solar Mars 100 | 10–11 | 10–15% (80–90% island) | 25% | DLE standard | Oil & gas optimized | UFLS coordination |
| Solar Titan 130 | 13.5 | 10–15% | 25% | DLE capable | Heavy-duty industrial | VAR margin 15–20% |
| Rolls-Royce RB211 | 25–30 | 10% (90–95% capable) | 30–35% | DLE with fast response | Aeroderivative heritage | Coordinated limiting |

Table Notes:
• Island Mode Derate reflects typical operational ceiling vs. ISO/base rating at same ambient temperature
• Step Load percentages are maximum acceptable for maintaining combustion stability (+ for load increase, - for decrease)
• All values represent industry best practices; specific project requirements may vary
• Black-start capability requires auxiliary systems (not included in base turbine specifications)
• DLE = Dry Low Emissions; DLN = Dry Low NOx (GE terminology)

# Strategies to Maximize Usable Island Mode Power

While the 10–15% island mode derate is standard industry practice, several strategies can maximize the usable power within safe operating limits:

## Power Factor Correction

Installing capacitor banks reduces the reactive burden on generators, freeing capacity for real power. Automatically switched capacitor banks respond to load changes, maintaining optimal power factor.

## Advanced Load Shedding Schemes

Well-designed UFLS with ROCOF-adaptive triggering allows turbines to operate at higher base loads by providing fast, reliable load reduction during generation loss events. Load prioritization ensures critical processes continue.

## Coordinated Multi-Unit Operation

Multiple smaller turbines in isochronous load-sharing mode provide better transient response than a single large unit. If one trips, the others can absorb the load more effectively. This allows higher aggregate loading (e.g., 90% vs. 85% for single-unit).

## Energy Storage Integration

Battery energy storage systems (BESS) can provide instantaneous power during transients (first 1–2 seconds), giving turbines time to respond. This effectively increases IRM and allows higher steady-state loading.

## Load Management and Demand Response

Interruptible loads and automated demand response reduce peak demand and provide controllable load reduction capability, reducing the required reserve margin.

## Governor and Excitation System Tuning

Optimizing governor response (proportional-integral-derivative gains) and AVR settings specifically for island operation improves transient performance. This must be done carefully to avoid instability.

## Combustion Control Optimization

Advanced fuel scheduling and active combustion monitoring can extend the stable DLE operating range, reducing the need for diffusion mode fallback and allowing operation closer to thermal limits.

## Key Principle

None of these strategies eliminates the need for headroom, but they can reduce the required margin from 15% to 10% or enable operation at the higher end of the range (90% vs. 85%) with acceptable risk.

# Conclusions and Industry Best Practices

## Summary of Key Findings

### Universal Industry Practice

All major OEMs (Kawasaki, GE, Siemens, Solar, Rolls-Royce) apply a 10–15% power derate for island mode operation relative to grid-parallel capability at the same ambient temperature. This derate is not thermal—it represents required control margin for stability, transient response, and protection.

### Physical Basis

The island mode derate exists because islanded turbines must:

- Maintain frequency without grid inertia support

- Supply all reactive power within generator capability limits

- Respond to load transients without external buffering

- Prevent DLE combustion flameout during rapid load changes

- Preserve headroom for load rejection and UFLS activation

### Typical Operating Limits

- Continuous island operation: 85–90% of ISO base rating

- Maximum step load increase: +25% of rated capacity

- Maximum step load decrease: –15% to –25% (controlled)

- Emergency load rejection: 100% (with automatic protection)

- Recommended steady-state power factor: 0.90–0.95 lagging

### Combustion Stability Critical

DLE systems impose step-load limitations. Exceeding ~25% step loads risks combustion instability, requiring automatic shift to diffusion combustion (higher emissions) or causing flameout and trip.

### Incremental Reserve Margin

Gas turbines can provide 10–15% of rated capacity within 1–2 seconds, plus ~0.5–1%/second thereafter. This IRM determines the maximum safe base loading in island mode.

## Best Practices for Island Mode Operation

### Design Phase

- Size generators with adequate MVA rating for reactive power demand (typically 115–120% of MW rating)

- Include power factor correction (capacitor banks or synchronous condensers)

- Design UFLS scheme with 4–6 stages, coordinated with governor response times

- Specify island mode capability in turbine procurement (controls, governors, protection)

- Plan for multi-unit operation when feasible (better transient response, n-1 redundancy)

### Operational Phase

- Limit continuous loading to 85–90% of rated output in island mode

- Maintain power factor above 0.90 (install/energize capacitor banks as needed)

- Avoid step loads exceeding 25% of turbine rating

- Monitor combustion mode (DLE vs. diffusion) and remain in DLE >50% load when possible

- Test UFLS schemes periodically; verify load shedding relays and sequencing

- Conduct annual block-load testing to verify transient response and step-load acceptance

- Train operators on island mode limitations and emergency response procedures

### Control System Requirements

- Isochronous governor capability for single-unit island operation

- Isochronous load-sharing for multi-unit systems

- Automatic island detection and mode switching (grid-parallel to island transition)

- Coordinated excitation limiting (OEL/UEL) with capability curve

- Combustion mode management (automatic DLE/diffusion switching)

- Interface to plant load-shedding system (UFLS coordination)

### Maintenance and Testing

- Verify governor response annually (step-load tests)

- Calibrate UFLS relays and test sequencing logic

- Inspect and test excitation system components

- Monitor combustion dynamics sensors (if equipped)

- Review and update load-shedding priorities based on operational changes

# References

Beckwith Electric. (2025). Generator protection theory. Power Plant Protection Track. Retrieved from https://beckwithelectric.com

British Petroleum. (2020). BP statistical review of world energy 2020. BP Statistical Review.

Cossé, R. E., & Nguyen, T. P. (2009). Gas turbine generator governor speed/voltage control for non-complex, islanding operating systems – "Which control strategy should I use?" IEEE Petroleum and Chemical Industry Conference.

Faqih, M., Omar, M. B., Ibrahim, R., & Omar, B. A. A. (2022). Dry-low emission gas turbine technology: Recent trends and challenges. Applied Sciences, 12(21), 10922. https://doi.org/10.3390/app122110922

GE Vernova. (2024). 6B gas turbine specifications. Retrieved from https://www.gevernova.com/gas-power/products/gas-turbines/6b

Hamilton, E. R., Undrill, J., Hamer, P. S., & Manson, S. (2009). Considerations for generation in an islanded operation. Presented at the 56th Annual Petroleum and Chemical Industry Conference. Published in Synchronous Generator Protection and Control: A Collection of Technical Papers Representing Modern Solutions, 2019. Schweitzer Engineering Laboratories.

Hitachi Energy. (2024). Synchronous condenser system. Retrieved from https://www.hitachienergy.com

Idaho National Laboratory. (2024). Shunt-connected FACTS and synchronous condensers (INL/RPT-24-78445). Idaho Falls, ID: Idaho National Laboratory.

IEEE Power System Relay Committee. (2019). Coordination of generator protection with generator excitation control and generator capability. Working Group J-5, Rotating Machinery Subcommittee.

IEEE Standards Association. (2025). IEEE 2030.12-2025: IEEE guide for the design of microgrid protection systems. IEEE Standards Association.

IEEE Standards Association. (2003). IEEE Std C37.106-2003: IEEE guide for abnormal frequency protection for power generating plants. IEEE Standards Association.

Kawasaki Heavy Industries. (2025). Z77-2B-25-088 Rev.0: L20A technical information for S&S. Kawasaki Gas Turbine Documentation.

Kawasaki Heavy Industries. (2001). First 20 MW gas turbine with 35% efficiency. Press Release. Retrieved from https://global.kawasaki.com

Kawasaki Heavy Industries. (2026). Z77-2B-26-014 Rev.0: Information about performance calculation and condition for island operation. Project Documentation.

Kawasaki Heavy Industries. (2005). Kawasaki L20A gas turbine. Bulletin of GTSJ, 2005. Gas Turbine Society of Japan.

Mitsubishi Heavy Industries. (2023). Next-generation gas turbine control for high ramp rate and stable combustion. Mitsubishi Heavy Industries Technical Review, 60(1).

Mitsubishi Power. (2021). Isochronous load sharing fact sheet for FT8 and FT4000 gas turbine units. Mitsubishi Power Systems.

Moloudi, M., & Mazinan, A. H. (2019). Controlling disturbances of islanding in a gas power plant via fuzzy-based neural network approach with a focus on load-shedding system. Complex & Intelligent Systems, 5, 79–89. https://doi.org/10.1007/s40747-018-0077-9

National Energy Technology Laboratory. (2003). Gas turbines in simple cycle & combined cycle applications. U.S. Department of Energy. Retrieved from https://www.netl.doe.gov

Petrotech, Inc. (2019). GE Frame 5 - Black start capabilities. White Paper. New Orleans, LA: Petrotech, Inc.

Schweitzer Engineering Laboratories. (2017). Isochronous load sharing principles for an islanded system with steam and gas turbine generators. Schweitzer Engineering Laboratories Technical Paper.

Sheldrake, A. L. (2003). Handbook of electrical engineering: For practitioners in the oil, gas and petrochemical industry. John Wiley & Sons. ISBN: 0-471-49631-6.

Siemens Energy. (2024). SGT-400 industrial gas turbine. Retrieved from https://www.siemens-energy.com/global/en/home/products-services/product/sgt-400.html

Siemens Energy. (2024). SGT-800 industrial gas turbine. Retrieved from https://www.siemens-energy.com

Siemens Energy. (2024). Synchronous condenser (SynCon) for grid stability and efficiency. Retrieved from https://www.siemens-energy.com

Solar Turbines. (2024). Turbine ratings. Caterpillar Solar Turbines. Retrieved from https://www.solarturbines.com

Tan, J., Dong, S., & Hoke, A. (2023). Island power systems with high levels of inverter-based resources: Stability and reliability challenges. Presented at ISGT 2023. National Renewable Energy Laboratory.

Woodward, Inc. (2018). Fuel metering systems for dry low emission (DLE) gas turbines (Application Note 83406). Woodward, Inc.